## Dashboard
Data Center Cooling Water Management — M&E Dashboard
50 MW IT design case · US customary units · yellow = input, green = live formula
Scenario & source controls
Water source | Municipal Potable |  | Dropdown — pulls Source Library column
Active scenario (Mass Balance view) | Corrugated Fill + High CoC |  | Dropdown — drives the Process Flow Mass Balance sheet
IT load | 50 | MW
Design wet-bulb temperature | 76 | °F
Average IT utilization | 80% | -
RO / IX demineralization on (1/0) | 0 | - | Skippable demineralization step
Scenario levers
Lever | Current Baseline | Corrugated Fill + High CoC | Unit
Target cycles of concentration (2–10) | 4 | 10 | cycles | Clipped by LEED/LSI/drift limits
Blowdown recovery RO on (1/0) | 0 | 1 | -
Key performance indicators
KPI | Current Baseline | Optimized | Δ (Opt − Base) | Unit
Cooling load |  |  |  | MW
Cooling load |  |  |  | tons
Tower heat-rejection load |  |  |  | tons
Chiller COP |  |  |  | -
Tower approach |  |  |  | °F
Cycles of concentration (operating) |  |  |  | cycles
Raw water intake |  |  |  | gpd
Raw water intake |  |  |  | m³/d
Evaporation loss |  |  |  | gpd
Drift loss |  |  |  | gpd
Blowdown (bleed-off) |  |  |  | gpd
Total discharge to sewer |  |  |  | gpd
WUE (water usage effectiveness) |  |  |  | L/kWh IT
Cooling + water plant power |  |  |  | kW
Cooling share of PUE |  |  |  | -
PUE (incl. other overhead) |  |  |  | -
Water-system energy intensity |  |  |  | kWh/m³
Annual operating cost (incl. carbon) |  |  |  | $/yr
CO₂e emissions |  |  |  | t/yr
LEED v4 WE cooling-tower points |  |  |  | pts
Legionella annual inhalation risk |  |  |  | per yr
Compliance & engineering checks
Check | Current Baseline | Optimized |  | Basis
CoC limiting constraint |  |  |  | LEED / LSI / drift / target
CoC feasible with this source |  |  |  | ≥ min CoC
Recirc silica |  |  |  | >150 mg/L alert
Recirc LSI (hot water) |  |  |  | ≤ inhibitor ceiling
LEED condenser limits |  |  |  | LEED v4 Table 1
Legionella Py ≤ target |  |  |  | 1e-4 /yr
Ingestion QMRA (all pathogens) |  |  |  | Beta-Poisson / exp.
Pumps in HI 9.6.3 POR |  |  |  | 0.7–1.2 × Q_BEP
System water balance closes |  |  |  | Intake = E + D + sewer
Upgrade investment (Baseline → Optimized)
CapEx (fill + eliminators + BD-RO + install) |  | $
Year-1 net operating savings |  | $/yr
NPV |  | $
IRR |  | -
Discounted break-even (BEP) |  | years
Simple payback (SPBT) |  | years
Water losses breakdown
Stream | Current Baseline | Optimized |  | Unit
Evaporation |  |  |  | gpd
Drift |  |  |  | gpd
Blowdown / brine to sewer |  |  |  | gpd
Treatment rejects |  |  |  | gpd
Annual cost breakdown
Cost item | Current Baseline | Optimized |  | Unit
Water purchase |  |  |  | $/yr
Sewer |  |  |  | $/yr
Electricity |  |  |  | $/yr
Chemicals |  |  |  | $/yr
Sludge disposal |  |  |  | $/yr
Carbon (SCC) |  |  |  | $/yr

## Process Flow Mass Balance
Process Flow Mass Balance — node by node
Q_out = Q_in − Q_reject − Q_evap ; C_out,j = [Q_in·C_in,j·(1 − R_j) + Dosing_j] / Q_out
1. Node configuration (toggle steps on/off)
Process step | On (1/0) | Recovery Q_out/Q_in | Energy kWh/kgal | LRV virus | LRV protozoa | LRV bacteria | pH out (blank = pass) | Effective recovery | Relative inflow Q_in/Q_intake | Energy used kWh/kgal
Raw Water Intake | 1 | 1 | 1.5 | 0 | 0 | 0 |  |  | 1
Coagulation / Flocculation / Sedimentation | 1 | 0.98 | 0.1 | 1 | 0.5 | 1
Multi-Media Filtration | 1 | 0.97 | 0.1 | 1 | 2 | 1
Ultrafiltration | 1 | 0.95 | 0.4 | 4 | 4 | 4
RO / IX Demineralization |  | 0.8 |  | 1.5 | 1.5 | 1.5 | 6.5
Chlorine Contact (CT) | 1 | 1 | 0.05 | 0 | 0 | 0
Overall train recovery Π(effective recovery) |  | -
Treatment energy per gallon of intake |  | kWh/gal | RO blank energy → 0.3 + 0.1·TDS(g/L) kWh/m³ (screening)
2. Coagulation / sedimentation — Stokes' law settling
Floc particle diameter | 150 | µm
Particle density ρp | 1065 | kg/m³
Water density ρw | 1000 | kg/m³
Dynamic viscosity μ (15 °C) | 0.00113 | Pa·s
Clarifier overflow rate | 1.5 | m/h
Design TSS removal | 90% | -
Settling velocity v_s = g(ρp − ρw)d²/(18μ) |  | m/s
Settling velocity |  | m/h
Achieved TSS removal = R_design × MIN(1, v_s/SOR) |  | -
Alum dose | 10 | mg/L
3. Removal fraction R_j (mass to waste) — RO row = 1 − Y·(1 − rejection)
Process step | EC | TDS | SiO₂ | Na⁺ | Ca²⁺ | Mg²⁺ | Cl⁻ | PO₄³⁻ | SO₄²⁻ | Alk (CaCO₃) | Free Cl₂ | TSS | BOD₅ | COD
RO membrane rejection (input) | 0.99 | 0.99 | 0.98 | 0.985 | 0.995 | 0.995 | 0.985 | 0.995 | 0.995 | 0.97 | 1 | 1 | 0.9 | 0.9
Raw Water Intake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coagulation / Flocculation / Sedimentation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 |  | 0.3 | 0.3
Multi-Media Filtration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.1 | 0.1
Ultrafiltration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.999 | 0.2 | 0.15
RO / IX Demineralization
Chlorine Contact (CT) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0
4. Chemical dosing (mg/L of node inflow; negative = consumed)
Process step | EC | TDS | SiO₂ | Na⁺ | Ca²⁺ | Mg²⁺ | Cl⁻ | PO₄³⁻ | SO₄²⁻ | Alk (CaCO₃) | Free Cl₂ | TSS | BOD₅ | COD
Raw Water Intake | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coagulation / Flocculation / Sedimentation | 6 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4.85 | -5 | 0 | 0 | 0 | 0
Multi-Media Filtration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ultrafiltration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RO / IX Demineralization | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chlorine Contact (CT) | 4 | 2.5 | 0 | 1 | 0 | 0 | 1.5 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0
5. Flow & quality matrix (active scenario) — C_out,j = [Q_in·C_in,j·(1−R_j) + Dosing_j]/Q_out with Q per unit intake
Process step | On | Inflow Q_in (gpd) | In pH | In EC | In TDS | In SiO₂ | In Na⁺ | In Ca²⁺ | In Mg²⁺ | In Cl⁻ | In PO₄³⁻ | In SO₄²⁻ | In Alk (CaCO₃) | In Free Cl₂ | In TSS | In BOD₅ | In COD | Reject / losses (gpd) | Evaporation (gpd) | Outflow Q_out (gpd) | Out pH | Out EC | Out TDS | Out SiO₂ | Out Na⁺ | Out Ca²⁺ | Out Mg²⁺ | Out Cl⁻ | Out PO₄³⁻ | Out SO₄²⁻ | Out Alk (CaCO₃) | Out Free Cl₂ | Out TSS | Out BOD₅ | Out COD | Flow balance check | TSS removed (kg/gal intake)
Raw Water Intake | [18 empty] | 0
Coagulation / Flocculation / Sedimentation | [18 empty] | 0
Multi-Media Filtration | [18 empty] | 0
Ultrafiltration | [18 empty] | 0
RO / IX Demineralization | [18 empty] | 0
Chlorine Contact (CT) | [18 empty] | 0
Cooling Tower (recirculation → blowdown) | bar: EC to SO₄²⁻
Blowdown Recovery RO (permeate → makeup) | [18 empty] | 0
System check: Intake − Evaporation − Drift − Sewer discharges | TDS: gpd; SiO₂: Must be 0 — whole-plant water balance

## Cooling Tower & Corrugated Fill
Cooling Tower Heat Balance & Corrugated Fill Simulation
Q = ṁ·cp·ΔT · Tower Load = Q(1 + 1/COP) · E = TL/(970×8.34) · B = (E − (N−1)D)/(N·k − 1 + Y)
1. Shared design inputs
Other heat to chilled water (fraction of IT) | 5% | -
Chilled-water ΔT | 12 | °F
Chiller COP at reference CWST | 5.5 | -
Reference condenser-water supply temp | 85 | °F
COP sensitivity per °F colder CWST | 2% | 1/°F | Screening ~2 %/°F
Non-cooling PUE overhead | 0.08 | -
Tower range (hot − cold) | 10 | °F
Water/air mass ratio L/G | 1.2 | -
Barometric pressure | 101.325 | kPa
Minimum CoC | 1.2 | cycles
Max recirculating LSI (inhibitor program) | 2.5 | -
Recirculating free-chlorine residual | 0.5 | mg/L
Silica blowdown alert | 150 | mg/L
Blowdown-recovery RO recovery Y | 70% | -
LEED max Ca (as CaCO3) | 1000 | ppm | LEED v4 WE Cooling Tower Water Use, Table 1
LEED max alkalinity | 1000 | ppm | LEED v4 WE Cooling Tower Water Use, Table 1
LEED max SiO₂ | 100 | ppm | LEED v4 WE Cooling Tower Water Use, Table 1
LEED max chloride | 250 | ppm | LEED v4 WE Cooling Tower Water Use, Table 1
LEED max conductivity | 2000 | µS/cm | LEED v4 WE Cooling Tower Water Use, Table 1
Fill model c0 (KaV/L at reference) | 1.2 | - | Screening calibration
Reference SSA | 150 | m²/m³
Reference fill height | 1.2 | m
KaV/L exponent on L/G (n) | 0.6 | -
Flute-angle thermal exponent | 0.15 | -
2. Scenario inputs — fill, drift eliminator, chemistry
Parameter | Current Baseline | Corrugated Fill + High CoC | Unit | Note
Fill / eliminator description | Legacy offset film fill + blade eliminator | Cross-fluted corrugated fill + cellular HE eliminator
Specific surface area (SSA) | 150 | 226 | m²/m³
Flute angle | 30 | 60 | °
Sheet thickness | 0.25 | 0.38 | mm
Fill height | 1 | 1.2 | m
Drift fraction of recirculation | 0.2% | 0.001% | - | 0.20 % → 0.001 % with HE eliminator
Drift eliminator pressure drop | 10 | 20 | Pa
Recirculating pH | 8.3 | 8.4 | -
Target CoC (from Dashboard) |  |  | cycles
Blowdown recovery on (from Dashboard) |  |  | -
3. Heat balance
Cooling load Q = IT × 3412 × (1 + other) |  |  | BTU/hr
Cooling load |  |  | MW
Cooling load |  |  | tons
Fill KaV/L available = c0(SSA/SSAref)(H/Href)(θ/30)^a(L/G)^−n |  |  | -
Cold-water temperature (Merkel solver, interpolated) |  |  | °F | Required KaV/L = available (Chebyshev)
Approach (cold water − wet bulb) |  |  | °F
Hot-water temperature |  |  | °F
Hot-water temperature |  |  | °C
Cold-water temperature |  |  | °C
Chiller COP = COPref·(1 + s·(CWSTref − CWST)) |  |  | -
Chiller power |  |  | kW
Tower Load = Q·(1 + 1/COP) |  |  | BTU/hr
Tower Load |  |  | tons
Recirculation Q = TL/(8.34·60·Range) |  |  | gpm
Evaporation E = TL/(970 × 8.34) |  |  | gph
Evaporation |  |  | gpd
Drift D = f_drift × Q_recirc |  |  | gpd
4. Cycles of concentration — limits on treated makeup
Constraint | Current Baseline | Corrugated Fill + High CoC | Unit | Basis
Target |  |  | cycles
LEED Ca (as CaCO3) |  |  | cycles
LEED alkalinity |  |  | cycles
LEED SiO₂ |  |  | cycles
LEED chloride |  |  | cycles
LEED conductivity |  |  | cycles
LSI ceiling: 10^((LSImax − pHr + pHs₁)/1.9) |  |  | cycles
Drift (bleed ≥ 0): 1 + E/D |  |  | cycles
Most restrictive limit |  |  | cycles
Limiting constraint
Operating CoC = MAX(min CoC, limit) |  |  | cycles
5. Tower & blowdown-recovery water balance
BD-RO recovery used Y |  |  | -
TDS mass fraction to brine k |  |  | -
Blowdown B = (E − (N−1)D)/(N·k − 1 + Y) |  |  | gpd
Course check: B = E/(CoC − 1) |  |  | gpd | Drift lumped into B; recovery off
Permeate recycled P = Y·B |  |  | gpd
Brine / blowdown to sewer |  |  | gpd
Fresh makeup M_f = E + D + brine |  |  | gpd
Tower makeup M_t = M_f + P |  |  | gpd
Raw water intake = M_f / Π recovery |  |  | gpd
Raw water intake |  |  | m³/d
Treatment rejects |  |  | gpd
Total discharge to sewer |  |  | gpd
WUE = intake / IT energy |  |  | L/kWh
6. Recirculating chemistry C_r,j = M_f·C_f,j / (D + B·k_j)
Species | Treated makeup C_f | BD-RO rejection | k (Base) | C_recirc (Base) | C_permeate (Base) | C_brine (Base) | C_blend (Base) | k (Opt) | C_recirc (Opt) | C_permeate (Opt) | C_brine (Opt) | C_blend (Opt)
pH
EC |  | 0.98
TDS |  | 0.98
SiO₂ |  | 0.97
Na⁺ |  | 0.97
Ca²⁺ |  | 0.99
Mg²⁺ |  | 0.99
Cl⁻ |  | 0.97
PO₄³⁻ |  | 0.99
SO₄²⁻ |  | 0.99
Alk (CaCO₃) |  | 0.95
Free Cl₂ |  | 1
TSS |  | 1
BOD₅ |  | 0.9
COD |  | 0.9
7. Scaling indices, silica & LEED v4 WE credit
Index | Current Baseline | Corrugated Fill + High CoC | Unit | Status / basis
Makeup pHs (cold water) |  |  | -
Makeup LSI = pH − pHs |  |  | -
Recirc pHs (cold water) |  |  | -
Recirc LSI (cold water) |  |  | -
Recirc pHs (hot water) |  |  | -
Recirc LSI (hot water) |  |  | -
Recirc RSI = 2pHs − pH (hot water) |  |  | -
LSI status
RSI status
Silica check
All LEED Table 1 limits met (1/0) |  |  | -
LEED max cycles (≤ 10) |  |  | cycles
Recycled non-potable share of makeup |  |  | -
LEED v4 WE Cooling Tower Water Use points |  |  | pts | 1 pt: max cycles; 2 pts: ≥10 cycles w/ treatment or ≥20 % recycled
8. Corrugated fill impact — Baseline vs Upgrade
Approach improvement |  | °F
COP improvement |  | -
Evaporation reduction |  | gpd
Drift reduction |  | gpd
Blowdown-to-sewer reduction |  | gpd
Raw water saved |  | gpd
Fan static pressure increase |  | Pa
Fan power change |  | kW
Chiller power saved |  | kW
[6 empty] | Stream | Baseline | Optimized
Evaporation
Drift
Sewer
Intake

## Pumping & Fan Hydraulics
Pumping & Induced-Draft Fan Hydraulics
WHP = Q·TDH/3960 · BHP = WHP/η_h · kW = BHP·0.7457/(η_m·η_e) · N = ROUNDUP(Q/Q_BEP) · POR 0.7–1.2 Q_BEP
1. Fan & fill air-side inputs
Tower water loading | 6 | gpm/ft²
Exhaust air specific volume | 14 | ft³/lb
Air density | 1.15 | kg/m³
Other static pressure (louvers, plenum, exit) | 60 | Pa
Fan efficiency | 75% | -
Fan motor efficiency | 94% | -
Fill ΔP coefficient c | 0.06 | - | Screening calibration
Fill ΔP flute-angle exponent | 0.5 | -
2. Induced-draft fan energy
Parameter | Current Baseline | Corrugated Fill + High CoC | Unit | Formula
Tower plan area |  |  | m² | Q_recirc / loading
Air mass flow G = L/(L/G) |  |  | lb/hr
Airflow |  |  | cfm
Airflow |  |  | m³/s
Fill face velocity |  |  | m/s
Fill open area ε = 1 − SSA·t/2 |  |  | -
Fill ΔP = c·SSA·H·½ρv²·(θ/30)^b/ε² |  |  | Pa
Total static pressure |  |  | Pa
Total static pressure |  |  | in. w.g.
IDF fan power = V·ΔP/(η_f·η_m) |  |  | kW
3. Pump stations (both scenarios)
Pump station | Scenario | Flow Q (gpm) | TDH (ft) | Q_BEP (gpm) | η hydraulic | η mechanical | η electrical | N = ROUNDUP(Q/Q_BEP) | Q per pump | POR min | POR max | In POR? | WHP | BHP | kW
Chilled-Water Pumps | Baseline |  | 120 | 3000 | 82% | 98% | 95%
Chilled-Water Pumps | Optimized
Condenser-Water Pumps | Baseline |  | 80 | 4000 | 84% | 98% | 95%
Condenser-Water Pumps | Optimized
Raw/Makeup Water Pumps | Baseline |  | 150 | 300 | 70% | 98% | 92%
Raw/Makeup Water Pumps | Optimized
4. Plant power summary
Component | Current Baseline | Corrugated Fill + High CoC | Unit
Chiller compressors |  |  | kW
Tower fans |  |  | kW
Chilled-water pumps |  |  | kW
Condenser-water pumps |  |  | kW
Raw/makeup water pumps |  |  | kW
BD-RO energy |  |  | kWh/d
Water treatment (train + BD-RO) |  |  | kW
Total cooling + water plant |  |  | kW
Cooling share of PUE |  |  | -
PUE |  |  | -
Water-system energy intensity |  |  | kWh/m³
All pumps in POR (1/0)

## Disinfection & Microbial Risk
Disinfection CT & Quantitative Microbial Risk Assessment
CT = C·T10 · T10 = TDT·BF · LRT = LOG(C_in/C_target) · Pd = 1 − (1 + d/β)^−α · Py = 1 − (1 − Pd)^n
1. Chlorine contact inputs
Contact tank operating volume | 100000 | gal
Peak flow factor | 1.5 | -
Baffling factor BF (0.1 unbaffled – 0.9 plug flow) | 0.3 | -
Water temperature | 20 | °C
Free chlorine residual (Mass Balance outlet) |  | mg/L
2. CT required lookup (free chlorine, SWTR Guidance Manual)
Temp (°C) | CT 4-log virus |  | Temp (°C) | CT 3-log Giardia (pH 7)
0.5 | 12 |  | 5 | 149
5 | 8 |  | 10 | 112
10 | 6 |  | 15 | 75
15 | 4 |  | 20 | 56
20 | 3 |  | 25 | 37
25 | 2
3. CT verification
Parameter | Current Baseline | Corrugated Fill + High CoC | Unit | Formula
Contact flow (train) |  |  | gpd
Peak flow Q_peak |  |  | gpm
Total detention time TDT = V/Q_peak |  |  | min
T10 = TDT × BF |  |  | min
CT = C × T10 |  |  | mg·min/L
CT required 4-log virus |  |  | mg·min/L
CT required 3-log Giardia |  |  | mg·min/L
Virus inactivation credit = MIN(4, 4·CT/CTreq) |  |  | log
Giardia inactivation credit = MIN(3, 3·CT/CTreq) |  |  | log
4-log virus achieved?
4. Physical log-removal credits (enabled nodes, Mass Balance sheet)
Virus LRV (Σ on × LRV) |  | log
Protozoa LRV |  | log
Bacteria LRV |  | log
5. Ingestion QMRA (worker exposure to cooling water)
Target annual risk Py | 0.0001 | per yr
Ingested volume per event | 1e-05 | L | WERF Table 3-1
Events per year n | 250 | 1/yr
Allowable per-event risk Pd = 1 − (1 − Py)^(1/n) |  | -
Pathogen | Model | α | β | r | LRV class | C source | Allowable dose d | C target | LRT required | LRV Base | Py Base | Check Base | LRV Opt | Py Opt | Check Opt
Rotavirus | beta_poisson | 0.253 | 0.422 | 0 | virus
Giardia | exponential | 0 | 0 | 0.0199 | protozoa
Cryptosporidium | exponential | 0 | 0 | 0.004191 | protozoa
Vibrio cholerae | beta_poisson | 0.097 | 13020 | 0 | bacteria
All ingestion pathogens meet target (1/0)
6. Legionella inhalation QMRA — drift aerosol (exponential, r = 0.06)
Recirculating Legionella (control level) | 1000 | CFU/L
Receptor plume dilution | 0.01 | - | Screening
Respirable fraction of drift water | 0.1 | - | Screening
Breathing rate | 1.3 | m³/h
Exposure duration per event | 1 | h
Events per year | 250 | 1/yr
Dose-response r | 0.06 | - | Armstrong & Haas (2007)
Parameter | Current Baseline | Corrugated Fill + High CoC | Unit | Formula
Aerosol water at receptor |  |  | L/m³
Inhaled water-equivalent volume |  |  | L/event
Dose d = C × V |  |  | CFU
Pd = 1 − EXP(−r·d) |  |  | -
Py = 1 − (1 − Pd)^n |  |  | per yr
Allowable recirculating Legionella |  |  | CFU/L
Required additional LRT on recirc water |  |  | log
Legionella risk check

## Financial & LCC Analysis
Financial & Lifecycle Cost Analysis (NYC DEP FY2022 tariffs)
i = r_interest + r_inflation · PV = FV/(1+i)^n · NPV = Σ CF_t/(1+i)^t − CapEx · SPBT = CapEx / savings
1. Tariffs, prices & finance inputs
Water rate | 4.1 | $/100 ft³ | NYC DEP FY22 metered water
Water rate |  | $/kgal
Sewer charge multiplier | 1.59 | × water | 159 % of water charge
Sewer rate |  | $/kgal
Cooling-tower sewer allowance (evaporation exempt) 1/0 | 1 | -
Electricity | 0.2 | $/kWh
Sodium hypochlorite (as Cl₂) | 0.6 | $/kg
Alum | 0.35 | $/kg
Scale/corrosion inhibitor | 3 | $/kg
Sludge disposal | 150 | $/dry ton
Alum sludge yield | 0.26 | kg/kg
Tower biocide dose (per makeup) | 2 | mg/L
Inhibitor held in recirculation | 10 | mg/L
Grid emission factor | 0.88 | lb CO₂/kWh
Social cost of carbon | 142 | $/t
Hours per year | 8760 | h
Operating days equivalent = hours/24 × utilization |  | d/yr
Interest rate | 4% | -
Inflation rate | 3% | -
Discount rate i = interest + inflation |  | -
Utility cost escalation | 2.76% | - | NYC water rate +2.76 % (FY22)
Fill cost | 350 | $/m³
Drift eliminator cost | 120 | $/m²
Blowdown-recovery RO cost | 2 | $/gpd
Installation factor | 1.3 | ×
2. Annual quantities
Quantity | Current Baseline | Corrugated Fill + High CoC | Unit
Raw water intake |  |  | gal/yr
Sewer discharge |  |  | gal/yr
Electricity |  |  | kWh/yr
Alum |  |  | kg/yr
NaOCl (contact + tower biocide) |  |  | kg/yr
Inhibitor = C × (B + D) |  |  | kg/yr
Dry sludge |  |  | dry t/yr
CO₂e |  |  | t/yr
3. Annual operating cost (year 1)
Cost item | Current Baseline | Corrugated Fill + High CoC | Unit
Water purchase |  |  | $/yr
Sewer |  |  | $/yr
Electricity |  |  | $/yr
Chemicals |  |  | $/yr
Sludge disposal |  |  | $/yr
Carbon (social cost) |  |  | $/yr
TOTAL |  |  | $/yr
Year-1 net operating savings (Baseline − Optimized) |  | $/yr
4. Upgrade capital cost
Corrugated fill = area × height × $/m³ |  | $
HE drift eliminators = area × $/m² |  | $
Blowdown-recovery RO |  | $
Installation |  | $
TOTAL CapEx |  | $
5. 10-year discounted cash flow
Year t | Cash flow CF_t | Discount factor 1/(1+i)^t | PV = CF/(1+i)^t | Cumulative PV
0 |  | 1
1
2
3
4
5
6
7
8
9
10
NPV = −CapEx + NPV(i, CF₁…CF_N) |  | $
NPV check = Σ PV |  | $
IRR |  | -
Discounted break-even year (BEP) |  | years
Simple payback SPBT = CapEx / savings |  | years
Investment decision

## Source Library
Source Library — Raw Water Quality Matrices
Edit any yellow cell; the Dashboard source selector pulls the matching column.
Baseline quality by source
Parameter | Unit | Municipal Potable | Sea Water | River Water | Groundwater | MBR Permeate / Wastewater Reuse | Rainwater (roof harvest) | Selected source
pH | - | 7.2 | 8.1 | 7.6 | 7.3 | 7 | 6
EC | µS/cm | 110 | 53000 | 400 | 700 | 900 | 20
TDS | mg/L | 65 | 35000 | 260 | 455 | 585 | 13
SiO₂ | mg/L | 3.5 | 2 | 12 | 30 | 20 | 0.5
Na⁺ | mg/L | 10 | 10770 | 20 | 40 | 90 | 1
Ca²⁺ | mg/L | 7 | 412 | 40 | 90 | 50 | 1
Mg²⁺ | mg/L | 1.5 | 1290 | 10 | 25 | 15 | 0.3
Cl⁻ | mg/L | 15 | 19350 | 25 | 50 | 110 | 2
PO₄³⁻ | mg/L | 2 | 0.1 | 0.3 | 0.1 | 4 | 0.05
SO₄²⁻ | mg/L | 6 | 2710 | 40 | 60 | 70 | 2
Alk (CaCO₃) | mg/L | 15 | 116 | 110 | 250 | 120 | 5
Free Cl₂ | mg/L | 0.7 | 0 | 0 | 0 | 0 | 0
TSS | mg/L | 0.5 | 20 | 50 | 2 | 1 | 10
BOD₅ | mg/L | 0.5 | 3 | 4 | 1 | 3 | 2
COD | mg/L | 2 | 10 | 15 | 3 | 25 | 10
Rotavirus | org/L | 0 | 10 | 50 | 0.1 | 500 | 1
Giardia | cysts/L | 0 | 1 | 10 | 0.01 | 0.1 | 0.5
Cryptosporidium | oocysts/L | 0 | 1 | 5 | 0.01 | 0.1 | 0.5
Vibrio cholerae | CFU/L | 0 | 100 | 10 | 0 | 1 | 0
E. coli | CFU/100 mL | 0 | 100 | 1000 | 1 | 10 | 50
HPC | CFU/mL | 50 | 1000 | 5000 | 100 | 1000 | 500
Legionella pneumophila | CFU/L | 1 | 10 | 100 | 10 | 100 | 10
Purchased (utility tariff) 1/0 | - | 1 | 0 | 0 | 0 | 0 | 0
Recycled non-potable (LEED) 1/0 | - | 0 | 0 | 0 | 0 | 1 | 1

## Merkel Solver
Merkel Solver — required tower characteristic KaV/L vs cold-water temperature
KaV/L = Range/4 · Σ 1/(h_sat(T_i) − h_air,i), T_i = T_cold + {0.1,0.4,0.6,0.9}·Range (Chebyshev)
Inlet air enthalpy h_sat(T_wb) |  | BTU/lb
Approach (°F) | T_cold (°F) | Δh @0.1R | Δh @0.4R | Δh @0.6R | Δh @0.9R | Required KaV/L
0.1
0.2
0.3
0.4
0.5
0.6
0.7
0.8
0.9
1
1.1
1.2
1.3
1.4
1.5
1.6
1.7
1.8
1.9
2
2.1
2.2
2.3
2.4
2.5
2.6
2.7
2.8
2.9
3
3.1
3.2
3.3
3.4
3.5
3.6
3.7
3.8
3.9
4
4.1
4.2
4.3
4.4
4.5
4.6
4.7
4.8
4.9
5
5.1
5.2
5.3
5.4
5.5
5.6
5.7
5.8
5.9
6
6.1
6.2
6.3
6.4
6.5
6.6
6.7
6.8
6.9
7
7.1
7.2
7.3
7.4
7.5
7.6
7.7
7.8
7.9
8
8.1
8.2
8.3
8.4
8.5
8.6
8.7
8.8
8.9
9
9.1
9.2
9.3
9.4
9.5
9.6
9.7
9.8
9.9
10
10.1
10.2
10.3
10.4
10.5
10.6
10.7
10.8
10.9
11
11.1
11.2
11.3
11.4
11.5
11.6
11.7
11.8
11.9
12
12.1
12.2
12.3
12.4
12.5
12.6
12.7
12.8
12.9
13
13.1
13.2
13.3
13.4
13.5
13.6
13.7
13.8
13.9
14
14.1
14.2
14.3
14.4
14.5
14.6
14.7
14.8
14.9
15
15.1
15.2
15.3
15.4
15.5
15.6
15.7
15.8
15.9
16
16.1
16.2
16.3
16.4
16.5
16.6
16.7
16.8
16.9
17
17.1
17.2
17.3
17.4
17.5
17.6
17.7
17.8
17.9
18
18.1
18.2
18.3
18.4
18.5
18.6
18.7
18.8
18.9
19
19.1
19.2
19.3
19.4
19.5
19.6
19.7
19.8
19.9
20
20.1
20.2
20.3
20.4
20.5
20.6
20.7
20.8
20.9
21
21.1
21.2
21.3
21.4
21.5
21.6
21.7
21.8
21.9
22
22.1
22.2
22.3
22.4
22.5
22.6
22.7
22.8
22.9
23
23.1
23.2
23.3
23.4
23.5
23.6
23.7
23.8
23.9
24
24.1
24.2
24.3
24.4
24.5
24.6
24.7
24.8
24.9
25
25.1
25.2
25.3
25.4
25.5
25.6
25.7
25.8
25.9
26
26.1
26.2
26.3
26.4
26.5
26.6
26.7
26.8
26.9
27
27.1
27.2
27.3
27.4
27.5
27.6
27.7
27.8
27.9
28
28.1
28.2
28.3
28.4
28.5
28.6
28.7
28.8
28.9
29
29.1
29.2
29.3
29.4
29.5
29.6
29.7
29.8
29.9
30
30.1
30.2
30.3
30.4
30.5
30.6
30.7
30.8
30.9
31
31.1
31.2
31.3
31.4
31.5
31.6
31.7
31.8
31.9
32
32.1
32.2
32.3
32.4
32.5
32.6
32.7
32.8
32.9
33
33.1
33.2
33.3
33.4
33.5
33.6
33.7
33.8
33.9
34
34.1
34.2
34.3
34.4
34.5
34.6
34.7
34.8
34.9
35
35.1
35.2
35.3
35.4
35.5
35.6
35.7
35.8
35.9
36
36.1
36.2
36.3
36.4
36.5
36.6
36.7
36.8
36.9
37
37.1
37.2
37.3
37.4
37.5
37.6
37.7
37.8
37.9
38
38.1
38.2
38.3
38.4
38.5
38.6
38.7
38.8
38.9
39
39.1
39.2
39.3
39.4
39.5
39.6
39.7
39.8
39.9
40